### Chilled Water System - Insulation Specification

### Part 1 - General

### Scope of Work

The requirements for the thermal insulation of chilled water pipes, including flanges, valves and other fittings that shall be insulated for condensation control and energy saving.

### Quality Assurance

Material shall be delivered in non-broken, factory furnished packaging and stored in a clean, dry indoor space that provides protection against weather.

Installation shall be applied by qualified personnel trained in appropriate installation methods.

Insulation shall not be applied until all surfaces are clear, dry and free of dirt, dust, grease, moisture and debris.

Work shall be performed at the temperatures recommended by the product manufacturer.

The materials, components and completed installation shall confirm to any local, applicable standards at the time of tendering.

Progressive testing of the systems to be insulated shall have been completed, inspected and approved by the owners' representative before the insulation is applied.

### Part 2 - Materials

### General

All insulation materials shall be:

Supplied from factories that manufacture under certified management systems; they should have an ISO 9001 registered Quality Management System and ISO 14001:2004 Environmental Management System.

Shown to have low chemical emissions of both Total Volatile Organic Compounds (TVOCs) and Formaldehyde. Preferably, materials should hold GREENGUARD Indoor Air Quality (IAQ) Certification.

Manufactured without the use of CFCs, HFCs or HCFCs. They should by fibre-free and dust free, and resist mold and mildew.

Made of a closed-cell structure to prevent moisture from wicking, since moisture accumulation will reduce insulation performance.

Protected when installed outside and exposed to weather, with either a suitable weather resistant finish or metal cladding material.

Installed without a reflective foil covering. If a reflective foil is supplied on the insulation surface, then the insulation thickness must be increased to avoid condensation that can occur due to the surface’s low emission coefficient.

Installed according to the manufacturer’s recommendations.

### Part 3 - Insulation

### Thermal Insulation

Pipes, vessels and equipment shall be insulated throughout with Armaflex MC, or an equivalent elastomeric Nitrile-rubber foam insulation that is closed cell, flexible and has a built-in vapour barrier.

Pipes shall be insulated with Armaflex MC in pre-formed tubes. Pipes that are too large for tube insulation shall be insulated with Armaflex MC in sheet form.

Insulation must have a thermal conductivity of ≤ 0.034 W/(m.K) at 0°C and ≤ 0.036 W/(m.K) at 24°C when measured according to ASTM C 177, ASTM C 518 or EN ISO 8497. Insulation must have a Moisture Resistance Factor of µ ≥ 7,000 according to DIN 52615 or ≤ 0.02 Perm-inch according to ASTM E96 Procedure A.

Insulation must have an operational temperature range of -50°C to +105°C (tubes) and -50°C to +85°C (flat sheets).

Preferably the material shall incorporate Microban® anti-microbial protection to actively inhibit the growth of mould.

  - Protective Coverings

Protective coverings shall be installed on areas of insulation that are exposed to weather or subject to mechanical damage.

The protective covering shall be:

“Arma-Chek Silver” multi-layer laminate of aluminium, coated with a UV protective film and backed with a flexible PVC film. The material should be adhered with Armaflex 520 Adhesive or equivalent, and all joins and seams secured with “Arma-Chek Silver Tape”. Installation shall be in all cases to the manufacturer’s recommendations.

Or

High density rubber cladding of the “Arma-Chek R” type bonded using an appropriate full contact adhesive with a minimum 50 mm overlap at all butt joints and longitudinal seams.  A weather-proof mastic sealant shall be applied over all seams and joints.  All material shall be overlapped and staggered in such a way as to ensure a watershed is always provided. Installation shall be in all cases to the manufacturer’s recommendations.

All excess adhesive visible on the surface of the completed assembly shall be removed using an appropriate cleaning material.

Or

Metal cladding, comprised of coated sheet metal, with all external joints and fixings made weather-proof with silicone sealant.

### Part 4 – Installation

All pipes and fittings must be free of extraneous chemicals such as corrosive cleaners or building materials’ dust prior to the installation of the insulation. The insulation must be clean and dry prior to installation.

Insulation must be installed in an adequately ventilated area to ensure airflow. It may be necessary to increase insulation thickness if adequate ventilation is not present. Do not crowd the insulation; allow for adequate air movement as this can affect condensation control. A gap of 100 mm (4 inches) is recommended between insulated pipes and from adjacent surfaces.

For pre-formed insulation tubes, insulate each continuous run of piping with full-length tubes of insulation, with single pieces cut to complete the end of the run. Do not use cut pieces or scraps abutting each other. Insulation shall be pushed onto pipe, not pulled. All joins and seams shall be installed by Compression Fitting. Overlap insulation 5 – 10mm (¼”) at butt-edge seams and compress the edges into place. There should be no gaps present at any joins. All seams shall be vapour sealed with Armaflex 520 Adhesive or Armaflex 820 Adhesive applied to the butt-edges of the insulation.

Insulation seams shall be staggered when applying multiple layers of insulation.

All pipe insulation shall be continuous through wall and ceiling openings, except where fire-stop materials are required.

At the beginning, at every 4m to 6m, and at the ends of piping runs, the insulation shall be adhered directly to the pipe using a 50mm strip of adhesive.

All valves, flanges and fittings shall be insulated throughout, using Armaflex sheet or tube material at the same thickness as used for the insulation of the main pipework. Insulation shall be mitered, pre-adhered and longitudinally slit inside throat to fit over all tees and elbows or bends over 90°. For additional information, consult the Armaflex Application Manual.

All joints and mitered seams shall be made with full coverage of Armaflex® 520 adhesive or Armaflex 820 adhesive on both surfaces. Insulation shall not be stretched during the process.  On all cold pipe work it is critical that all seams and joints are glued in their entirety to provide a continuous vapour seal. Butt joints must be fitted under compression, and all seams and butt joints must be glued in their entirety to create a continuous vapour seal. The adhesive must be suitable for the operational temperatures of the system.

No additional external water vapour barrier shall be necessary with Armaflex, as the vapour barrier is built into the insulation material. The insulation material shall have a moisture resistance factor of µ ≥ 7,000 or ≤ 0.02 Perm-inch, with testing performed according to EN 12086, DIN 52615 or ASTM E96 Procedure A.

Saddles shall be insulated on all insulated lines at clamps, hangers, or locations where insulation may be compressed.

All hanging and clipping of pipes shall be made with Armafix pipe hangers and pipe supports, or with pipe supports made from the same material as the pipe insulation with the inclusion of a PUR/PIR bearing segments to support the pipe weight. The hangers and supports will be constructed from a suitable material to prevent compression. The pipe supports and hangers must be glued to the adjacent insulation to provide a vapour seal, and the completed assembly of suitable construction to prevent thermal bridging.  The seams shall be sealed with Armaflex 520 or 820 contact adhesive.

Hangers clamped directly to the pipe shall be insulated over the hanger; insulation shall be fully adhered to the hanger. In addition, hangers with double rods shall be insulated between the rods. All seams of the insulation shall be sealed with adhesive.

### Part 5 – Insulation Thickness Guidance Tables

Refer to Armaflex recommendations for pipe insulation thickness needed to prevent condensation. Thickness may be increased above these levels to meet energy saving objectives.

When cladding insulation with a reflective material, such as metal jacketing, the insulation thickness should allow for the lower surface coefficient of the material.